



-------------------------------,,- 

" 

... 

.. 

• .' 

: 

/ 'I 

[image: image1.png]



[image: image2.png]3 LABORATORIES





[image: image3.png]



[image: image4.png]



UNDERWRITERS LABORATORIES INC . 

NORTHBROOK. IL . MELVILLE. NY, SANTA CLARA. CA . TAMPA, FL 

an independent, not-for-profit organization testing for public safety 

File R10603 Project 83NKl1823 

August 5, 1983 

REPORT 

on 

FIRE RETARDANT COATINGS 

Fire Safe Chemical Corp. 

Fort Worth, TX 

Copyright ~ 1983 Underwriters Laboratories Inc. Underwriters Laboratories Inc. authorizes the above named company to reproduce this Report provided it is reproduced in its entirety. 

[image: image5.png]



UNDERWRITERS LABORATORIES INC . 

NORTHBROOK. IL . MELVILLE. NY, SANTA CLARA. CA . TAMPA, FL 

an independent, not-for-profit organization testing for public safety 

- 

File R10603 Project 83NKl1823 

August 5, 1983 

REPORT 

on 

FIRE RETARDANT COATINGS 

Fire Safe Chemical Corp. 

Fort Worth, TX 

Copyright ~ 1983 Underwriters Laboratories Inc. 

Underwriters Laboratories Inc. authorizes the above named company to reproduce this Report provided it is reproduced in its entirety. 

Pile R10603 

Page 1 

Issued: 8-5-83 

· '. 

D E S C R I P T I O N 

PRODUCTS COVERED: 

The products covered by this Report are fire retardant coatings. 

USE: 

The coatings covered in this Report are intended for use as interior coatinqs as permitted by the authorities having jurisdiction. The established Surface Burning Characteristics o£ the coatings are applicable only when the coating material is applied in the indicated number of coats, coverage rates, substrates, and overcoats and undercoats as specified in the published advices of Underwriters Laboratories Inc. and when the coating is maintained. 

NGS!RNW:ist 

File RI060J 

Page Tl-l 

Issued: 8-5-83 

1 

T E S T 

R E C O R D 

N O. 

EXAMINATION OF MATERIAL: 

The materials used in this investigation were produced 

in a ready-to-use form under the observation of a representative of Underwriters Laboratories Inc. and were applied to the indi​cated test surfaces at the Northbrook testing station. 

The compositions of the coating materials are of a proprietary nature and the formulas involved are on file at the Laboratories for use in the Follow-Up Service Program. 

Various chemical and physical analyses were conducted on the coating materials and the results obtained from these analyses were employed in the establishment of specifications for use in the Follow-up Service Program. 

SURFACE BURNING CHARACTERISTICS TESTS: 

SAMPLES 

Substrate

Douglas Fir - The test decks were 21 in. wide and 8 ft 

long, composed of 1 by 4 in. tongue-and-groove Douglas fir flooring fastened together on the unexposed surface with wood furring strips. Three such decks were butted together end to end to 

form the 24 ft long test surface required to fill the Steiner Tunnel furnace. 

Coatings

The coating materials were applied to the test surfaces by a representative of the submittor under the observation of a staff member of Underwriters Laboratories Inc. The coating materials were rolled applied in three coats; each coat was allowed to dry to touch before the application of the next. 

The amount of coating applied was determined by weight. 

Two coatings were evaluated under this investigation; 

for the purpose of this Report, the coatings have been identified as "Type C" and "Type I". "Type e" coating was applied at a 

rate of 360 ft2/gal per coat; "Type I" coating was applied at 

a rate of 330 ft2/gal per coat. 

The test samples were conditioned for 28 days at a temper​ature of 70 ± 5°F and relative humidity of 45 to 55 percent before testing. 

File Rl0603 

Page Tl-2 

Issued: 8-5-83 

METHOD 

The tests were conducted in accordance with the Standard of Underwriters Laboratories Inc., Tests for Surface Burning Characteristics of Building Materials, UL 723. 

RESULTS 

Data on flame spread, fuel contributed, and smoke developed appears in the following tabulations. 

Flame Spread 

The maximum distance the flame spreads along the length 

of the sample from the end of the igniting flame is determined by observation. The flame spread Classification of the material is ' derived by determining the area under the flame spread distance (ft) versus time (min) curve, ignoring any flame front recession, and using one of the calculation methods as described below: 

1. If the total area (AT) is less than or equal to 

97.5 min-ft (meter-minute x 3.3), the flame spread Classification is to be 0.515 times the total area (AT), FSC = 0.515 AT' 

2. If the total area (A~) is greater than 97.5 min-ft (meter-minute x 3.3), the flame spread Classification is to be 

4900 divided by 195 minus the total area (AT) I FSC = 4900/ (195-AT). 

Test No. 

Material 

Calculated Value For Flame Spread 

12123456 

Blank Douglas Fir Decks Blank Douglas Fir Decks Type C 

Type C 

Type C 

Type I 

Type I 

Type I 

66.4 77.5 21.2 22.7 23.0 36.9 34.6 36.8 

Fuel Contributed 

A time-temperature curve is developed by plotting the temperatures measured by a thermocouple located at the 23 ft point (vent end) in the furnace against time. The calculated value for fuel-contributed Classification is derived by expressing the net area under the curve for untreated red oak and asbestos-cement board. 

Test No. 

Calculated Value For Fuel Contributed 

File R10603 

Page T1-3 

Issued: 8-5-83 

Material 

Blank Douglas Fir Decks 

Blank Douglas Fir Decks 

Type C 

Type C 

Type C 

Type I 

Type I 

Type I 

NGS 

Blank Douglas Fir Decks 

Blank Douglas Fir Decks 

Type C 

Type C 

Type C 

Type I 

Type I 

Type I 

12 3 4 5 6 7 8 

71.2 71.8 14.0 13.7 15.2 30.2 29.8 26.1 

Smoke Developed 

The smoke developed during the test is indicated by the output of a photoelectric circuit operating across the furnace flue pipe. A curve is developed by plotting values of light absorption (decrease in cell output) against time. The calculated value for smoke-developed Classification is derived by expressing the net area under the curve for the material under test as a percentage of the net area under the curve for untreated red oak. 

Test No. 

12345678 
Calculated Value 

For Smoke Developed 

20.7 

18.4 148.5 131.6 144.4 101. 3 

    92.1

    92.1 

File R10603 

~DRFACE BURNING CHARACTERISTICS OF APPLIED COATINGS 

Page C2 

Issued: 8-5-83 

Douglas Fir 

Douglas Fir 

Surface 

Flame Spread Fuel Contributed Smoke Developed 

Number of preliminary coats 


- 
L 

Rate per coat (ft /gal) 

Number of fire retardant coats Rate per coat (ft2/gal) 

Number of overcoats 

Rate per coat (ft2/gal) 

Flash point of liquid coatings: 

Fire retardant coating: closed cup, no flash 

20 15 140 None
  - 

3 360 None
- 

35

30 95 

None
  - 

  3

330

None
 - 

[image: image6.png]Re/p’rzﬁ /
%N{{é)é/ {ANCH{’/

Projectt Engineer
Fire Protection Department




Reviewed by: 

[image: image7.png]ot D771 (el




RICHARD N. WALKE 

Engineering Team Leader 

Fire Protection Department 

NGS/RNW:ist 


