Report No. 720344

Fort Worth, Texas

Our letters ant! r-eports are for the exclu .. slve use of the client to whom the)' arc addressed and shall not be reproduced except in full without the approval of the testing laborator-y. The usc of our name must r-eceive our prior written approval. Our letter'S and reports apply only to the sample tested and/or Inspected, and are not uecessur-llj- indicative of the qualities of appar-ent! .... ldcuticul or shuilar products.

-----..._-----

Maxim Tech. • Southwestern Labs 2200 Gravel Drive Fort Worth, TX 76118-7123

TECHNOLOGIES INC

Telephone: (817) 284-7755 Metro: (817) 589-7211 Fax: (817) 589-1420

FIRE HAZARD EVALUATION USING THE MONSANTO TWO-FOOT FLAME TUNNEL

AND

SMOKE CHAMBER

Performed on

April 28, 1997

for Canbo, Inc.

Attention: Mr. Denis Girard

Asteco • Austin Research Engineers' Chen-Northern' Empire Soils Investigations. Kansas City Testing

Maxim Engineers. Nebraska Testing. Patzig Testing· Southwestern Laboratories. Thomas-Harfip • Twin City Testing

2

TECHNOLOGIES INC

FIRE HAZARD EVALUATION USING THE MONSANTO TWO-FOOT FLAME TUNNEL AND SMOKE CHAMBER

SAMPLE IDENTIFICATION:

Seventy Percent Flame Safe Wood Safe Solution, 2 X 4 M, N, and O. All samples were signed by Mr. Denis Girard.

SCOPE OF TESTING:

The purpose of this testing was to determine the protection a material affords its substrate and the comparative burning characteristics of coatings. The testing was accomplished using equipment and procedures to evaluate the flame spread over the surface of the material under controlled conditions. This establishes a basis for comparing surface-burning characteristics of different coatings without specific consideration of all the end-use parameters that might affect these characteristics under actual fire conditions.

In addition to the predicted flame spread rate, the afterflame time, afterglow time, smoldering and smoke developed rate may be measured. However, a relationship should hot be presumed among these measurements.

SIGNIFICANCE:

A number of laboratory procedures are used In evaluating the effectiveness of fire-retardant and fire-resistant treatments and coatings. In general these methods measure the three stages of fire development: (1) ignition, (2) flame spread (rate of growth of the fire), and (3) conflagration extent. While all three are of extreme importance, flame spread has been recognized as the main factor associated with testing fire-retardant coatings. The Two-Foot Tunnel apparatus as produced by the Monsanto Company has been designed specifically to predict the performance by the ASTM E-84 (Steiner Tunnel) equipment. Flame spread ratings based upon ASTM E-84 have acquired common acceptance by regulatory agencies, but such large scale tests are seldom practical during the development or modification of a fire-retardant coating.

Our letters and reports are for the exclusive use of the client to whom they are addressed and shall not be reproduced without the approval of the testing laboratory. The use of our name must receive our prior written approval.  Our letters and reports apply only to the sample tested and/or inspected, and are necessarily indicative of the qualities of apparently identical or similar products.

Asteco • Austin Research Engineers· Chen-Northern· Empire Soils Investigations. Kansas City Testing Maxim Engineers. Nebraska Testing. Patzig Testing· Southwestern Laboratories. Thcrnas-Hartiq • Twin City Testing

TECHNOLOGIES INC

3

This method provides the relative flame spread in comparison with standard materials. Results from the two-foot tunnel test have been shown to correlate to a predicted approximate ASTM E-84 r-e au Lt., according to the following equation:

y = 4.8 + O.92x

where x is the result obtained from the Monsanto test apparatus and y is the predicted result from ASTM E-84.

Degree of the density of the smoker particulate matterr and other effluent given off by the test specimen are continuously recorded during the flame spread test and rated as a percentage of the degree of smoke density of red oak. Comparative smoke density determinations are made by use of the Monsanto Smoke Chamber which was developed as an approximation of the smoke density equipment utilized in the ASTM E-84 equipment. No direct correlation data is available between smoke density results obtained by the Monsanto Chamber and those obtained by ASTM E-84.

TEST EQUIPMENT:

The Monsanto Two-Foot Flame Tunnel and Smoke Chamber consists of a 24 x 4 inch angle-iron flame inclined 28° from the horizontal. The sides and fire-end of the tunnel are covered with 1/4" asbestos-cement board which is attached to the inside of the frame. The open endr flue end and cutout sides allow a natural draft through the tunnel. Heatr gases and smoke rise by convection flow. The sample holder is notched along the bottom, or supporting lip angle at one inch intervals to assist in measurement of the flame advance. An observation window , a two-inch wide strip of 1/8" polished vycor plater is located just below the sample holder and extending the full length of the tunnel. The glass is calibrated every inch from 4 to 22. The burnerr using local commercial gas fuelr is placed 2 1/4" horizontally from the interior of the fire-end of the tunnel. A thermocouple, ignition transformerr time and regulating valve are part of the assembly.

The Smoke Chamber is equipped with a light source, photoelectric cell, milliampere recorder, necessary stacks, vents and accessories.

Test results are shown on the following page.

Asteco • Austin Research Engineers. Chen-Northern .• Empire Soils Investigations. Kansas City Testing Maxim Engineers. Nebraska Testing. Patzig Testing. Southwestern Laboratories. Thomas-Hartq » Twin City Testing

TECHNOLOGIES INC

4

TEST RESULTS:

Test and Calibration Data:

Tunnel is calibrated prior to each day's operation by determining the difference in flame length of standard preconditioned mineral board and red oak boards.

Data

Flame Length (L) (Average of three highest consecutive flame front readings)

Flame Spread (FS) (Flame length of test panel minus flame length of mineral board calibration panel)

Flame Spread Constant (k)

(100) Lo - La

( 100 (17.3-8.5)

)

= 11.36

EVALUATION OF TEST DATA:

Determination

Monsanto Flame Spread Rating (FS multiplied by k )

FLAME SPREAD - Predicted E-84 value by use of Monsanto formula

Afterflaming

Afterglow

Smoldering

Smoke Developed Rating

reported as a percentage

of smoke developed by the

Red Oak Calibration Panel      47         47		 56		50

Calibration Panels Mineral

Red Oak 	Board

17.3

8.5

Test Specimen No.1 No.2 No.3

9.5 10.0 9.75

1.0 1.5 1.25

Test Specimen

No. 3 	Avg.

17.2 	14.2

17.9 	17.9

None 	None

None 	None

None 	None

Test Specimen No.1

Test Specimen No.2

Asteco • Austin Research Engineers • Chen;Northern ·EmPire · Soils Investigations 0 Kansas City Testing

Maxim Engineers. Nebraska Testing. Patzig Testing, Southwestern Laboratories. Thornas-Hartq- Twin City Testing

11. 4

17.0

15.3

20.4

None

None

None

None

None

None

TECHNOLOGIES INC

5

Note:

This test report contains only findings and results arrived at after employing the specified procedures listed herein. These findings and results apply only to the submitted sample or samples. This test report is not intended to constitute a recommendation for, or endorsement of, the product or material tested.

References:

ASTM D3806, Small-scale Evaluation of Fire Retardant Paints (Two-Foot Tunnel Method)

ERDL Report No. 1226, Report No. 111939 Department of Commerce Vandersall, H.L., Journal of Paint Technology, Volume 39, No. 511494, Interior Federal Specification TT-P-00193Z (GSA-FSS) Harland, W.J. Journal of Paint Technology, Vol. 44, No. 57564.

Technician:

Les Hall, S.E.T.

Sincerely,

SOUTHWESTERN LABORATORIES

Tim Begole Operations Manager

tm